
SUBJECT:	HONEST COMPANY PLAYA VISTA OFFICE
ADDRESS: 12121 BLUFF CREEK DRIVE  

Drawings Dated:  08/11/2026
Drawing Reference: E0.01 TO E6.7-2
Addendum: None

BASE BID								$0.00


Inclusions:

1. Power Distribution:
· Provide and install (3) 100A/3P and (1) 125A/3P circuit breaker on existing panel boards as shown on single line diagram.
· Provide (2) sub-meter as shown on single line diagram.
· Provide and install new panel boards 5L1A2LAB, 5L1A2MDF, 5L1B1A and 5L1B2A  as shown on single line diagram.
· Demo existing feeder that feeds existing panel LPAA and LPBB
· Provide and install (1) 1 1/4” C EMT with 4#2, 1#8 from existing panel 5L1A2 to new panel 5L1A2LAB (65LF).
· Provide and install (1) 1 1/4” C EMT with 4#2, 1#8 from existing panel 5L1B1 to new panel 5L1B1A (10LF).
· Provide and install (1) 1 1/4” C EMT with 4#2, 1#8 from existing panel 5L1B2 to new panel 5L1B2A (10LF).
· Provide and install (1) 1 1/2” C EMT with 4#1, 1#6 from existing panel 5L1A2 to new panel 5L1A2MDF (70LF).

2. Lighting Plan:
· Provide and install lighting fixtures as shown on lighting plan.
· Provide and install lighting control devices as shown on lighting plan.
· Provide title 24 acceptance certification.
3. Power Plan: 
· Provide and install power devices with branch wiring as shown on plans.
· Provide and install poke thru devices as shown on plans.
· Provide and install disconnect switches for mechanical devices as shown on plans.
4. LV, AV and SEC Rough: 
· Provide and install back box and conduit stub with pull string for low voltage devices as shown on plans.
· Provide and install back box and conduit stub with pull string for security devices as shown on plans.
· Provide and install back box and conduit stub with pull string for security devices as shown on plans.
· Provide and install cable tray in the corridors as shown on plans. All cable trays inside the IDF and MDF will be provided and installed by LV contractor.
5. Temp power and lighting: 
· Provide temporary power and lighting.
6. Clarifications: 
· All work to be performed during regular working hours.
· Low voltage devices, wiring and termination are excluded.
· Security devices, wiring and termination are excluded.
· AV devices, wiring and termination are excluded.
· Fire alarm devices, conduit, wiring and termination are excluded.
· Parking fees are excluded. See alternate adder.
· Safe off and demolition is excluded.


Project Specific Exclusions: 
· Electrical Permits
· Engineering and plan check fees
· Utility company charges or fees
· Temporary power and lighting
· Replace or upgrade existing panel boards.
· Low voltage devices, wiring and termination
· Security devices, conduit, wiring and termination
· Fire alarm devices, conduit, wiring and termination
· Access panels
· Overtime/ Shiftwork
· Unforeseen or bringing existing conditions into current code compliance
· Installing roof flashings, sealing of roof penetrations or any waterproofing
· Structural supports or structural engineering for any type of equipment 
· Accelerated or compressed working schedule
· Concrete saw cutting, breaking removal and repair
· X-ray or Sonar of surfaces for penetration
· Patching and painting of all surfaces
· Poured and formed concrete or asphalt
· Demolition and removal or cutting walls
· Mechanical controls, panels, relays, VFDs, control conduit and wire
· Temporary task lighting, equipment connections or generators 
· Removing trash, excavation spoils or demolished derbies off-site  
· Special inspection fees including after normal work hour inspections
· Custom fixture colors not listed on this bid set of documents
· Exit or emergency lighting not shown on electrical drawings
· Vapor barrier seal-offs, infection and/or dust control
· Providing or installing ceiling seismic wires 
· CAD As-builts, BIM or AutoCAD detailing 
· Finished surface protection or covers
· Ceiling, wall or floor access panels 





